## Slide 1: STEAM CAPACITY UPGRADING FOR BAGASSE FIRED BOILERS
Dr Terry Dixon
XXI Congreso De Tecnicos Azucareros
De Centroamerica
21 - 25 August 2017

## Slide 2: DIXON SOLUTIONS Pty Ltd Dr Terry Dixon

## Slide 3: TOPICS TO BE COVERED
Context of capacity Upgrading – absolute limit to factory crushing capacity options
Boiler Design Components
Physics of Boiler Design
Design Margins – fixed and flexible
Vendor options, market edge
What items can be changed or upgraded
Operational factors
History of capacity upgrades
Summary of Upgrading

## Slide 4: WHY CAPACITY UPGRADE
Inability to achieve design output (MCR)
Remove small boiler from service
Small increase for distillery steam supply
Increase crushing rate
Utilise margins in original design
Upgraded combustion capability
Steam is absolute limit of factory capacity options
ID Fans are absolute limit of boiler capacity options !

## Slide 5: BOILER CAPACITY MCR
MCR – Maximum Continuous Rating for stable normal operations – Design Capacity
What limits apply to MCR – there can be many !
Can a Boiler generate steam above MCR – YES !!!
What would be the limit to the increased steam capacity ? – depends on what specific boiler component or parameter is limiting …..

## Slide 6: BOILER CAPACITY LIMITS
Feedwater Pump – cannot deliver more water to the steam drum
FD Fan – no more air input
ID Fans – no more flue gas extraction – Furnace positive pressure & blowback
Bagasse Feeders – maximum speed; choking ?
Combustion – increased grate deposition; increased Unburnts carryover
Steam Separators – solids carryover into Superheater and outlet steam
Water Circulation – overheated tube rupture

## Slide 7: BOILER CROSS-SECTION

## Slide 8: LA GRECIA – Caldera #3

## Slide 9: BOILER COMPONENTS
Many components can be uprated or increase capacity (economically)
  - Bagasse Feeders
  - Feedwater Pumps
  - FD Fan
  - ID Fans
  - Superheaters
  - Steam Separators
  - Economiser (specific design)
  - Airheater
Some hard limits not economically justified

## Slide 10: CONTEXT OF CAPACITY UPRATING
No changes to major boiler components
- Furnace Geometry (width, depth)
- Pressure parts (drums, headers)
- Economisers (possible)
- Airheaters (possible)
Major focus on combustion system
- firing rate
- grate deposition / combustion cycling
- large particle combustion dynamics
Secondary Air modifications
- gas flow optimisation – CO removal
- Unburnt Carbon (UBC) burnout

## Slide 11: BOILER DESIGN CONSTRAINTS
Component Costs are large factor
Steam Pressure and Temperature
Evaporation and Superheat balance
Furnace Width (bagasse feeders, cost & design of drums, steam separators, grate)
Furnace Height (structure, FEGT)
Economiser (steaming)
Airheater (gas corrosion, efficiency)
Dust Collectors – Scrubber, ESP, MDC (statutory limits)

## Slide 12: DESIGN MARGINS
Fixed and Flexible Parameters
Design Criteria used by boiler OEM’s
Statutory Design Codes – Pressure Parts
Structural and Material margins
UG Air Temperature
SA Air Temperature (??)
Furnace Plan Area
Furnace Residence Time

## Slide 13: DESIGN MARGINS
Furnace Exit Gas Temperature – not a constraint for bagasse firing
(ash slagging/fouling in SH’s)
Economiser water exit temperature (no steaming)
Airheater gas exit temperature (corrosion)
Steam Separators

## Slide 14: VENDOR/OEM OPTIONS
Significant variations for key design concepts
Number of FD & ID Fans
Secondary Air configuration
Bagasse Feeder design
Bagasse Spreader system & Spreader position
Economiser layout
Airheater layout
Gas side flow baffles
Air side flow baffles

## Slide 15: COMPONENT CHANGES
Depends on % steam increase
10% up to 35%
Bagasse Spreader design, position, air ducting
Secondary Air rows, nozzles, position, flows
Superheater surface area
Steam separators
Safety Valves
BFP and FW Control Valve
FD Fans, ID Fans – blade tipping, new impellers
Flow Baffles in Gas and Air ducts

## Slide 16: GAS AND AIR BAFFLES
Gas Side Baffles
- Economiser Inlet
- Airheater Inlet first module
- Airheater cross-duct at bottom
- Airheater Outlet
- ESP Inlet
- ESP Outlet
Air Side Baffles
- Secondary Air Inlet Plenum
- Forced Draft Inlet Plenum
- Secondary Air Outlet Plenum
- Forced Draft Outlet Plenum
- Undergrate supply ducting
- Undergrate entry ducts

## Slide 17: TUBE METAL TEMPERATURES

## Slide 18: AIRHEATER - ECONOMISER
Tube Erosion and Tube Corrosion problems are caused by non-uniform gas, air and ash particle flows
Economisers have simultaneous high gas flows and high ash particle concentrations – high erosion
Airheaters have simultaneous low gas flows and high air flows – high corrosion
Airheater tube blockage and tube corrosion occur during normal operation
Airheater air bypass during boiler start-up does not stop tube corrosion – it achieves no benefit

## Slide 19: OPERATIONAL CHANGES
No changes to normal boiler operations
Set up bagasse spreaders correctly
Tune Master Pressure loop (bagasse feeders)
Tune FD airflow and Oxygen Trim loop
Attention to bagasse feeders to produce uniform bagasse flow to spreaders – no lumping / clumping
Optimise controls for mill stops and starts
Leave controls in AUTO !!!

## Slide 20: HISTORY CAPACITY UPGRADES
Major boiler modification (Mulgrave Australia)
Upgrade 180 tph – 240 tph (Pioneer Australia)
Upgrade steam conditions (depends on original boiler pressure design)
Circulation analysis (upgrade downcomers ?)
Large increases – larger ID Fans
Large increases – SA system modifications, larger FD and ID Fans, larger BFP etc.
Furnace waterwall expansion
Add / Increase Economiser surface
Small increases (10%) within ID/FD Fans

## Slide 21: SUMMARY
Combustion system must be tuned
- Bagasse spreader settings
- Undergrate air distribution
- Rear wall Secondary Air
10–15% increase with FD, ID Fans only
Larger capacity increases
- New FD, ID Fans, BFW Pumps
- Circulation
- Furnace Plan Area / Volume
- Secondary Air
- Economisers / Airheaters / ESP

## Slide 22: THANK YOU
QUESTIONS ?

## Slide 23: B
M